## Instructions
MagnaDRY® Tool
Purpose: | Calculate & compare the leaving air conditions and moisture removal of a MagnaDRY® Unit
Assumptions: | Latent heat of Water hfg = 1065 BTU/lb @ 50°F
Weight of water WtH20 = 8.3 lbs/gal
Motor "watts" will result in additional temperature rise
(motor power is not considered in the calculations below)
Procedure:
| Step 1 | Input entering dry bulb (DB) temperature.
| Step 2 | Input entering wet bulb (WB) temperature.
| Step 3 | Input outside ambient temperature.
| Step 4 | Input Total Capacity (TC) from product technical guide.
| Step 5 | Input Sensible Capacity (SC) from product technical guide.
| Step 6 | Input operating airflow (CFM)
| Step 7 | View moisture removal in lb/hr or gal/hr.
| Step 8 | View change in Sensible Cooling (Change in temperature)
| Step 9 | View change in leaving dry bulb (DB) temperature.
| Step 10 | View change in leaving wet bulb (WB) temperature.
Example 1:
| DR048 Normal Mode |  | DR048 Reheat Mode
| Conditions 95°F, 80/67°F |  | Conditions 95°F, 80/67°F
| CFM = 1600 |  | CFM = 1600
| TC = 47.8 KBTU |  | TC = 35.1 KBTU
| SC = 35.5 KBTU |  | SC = 21.4 KBTU
| Latent = 12.3 KBTU |  | Latent = 13.7 KBTU
| 12300 BTU/hr |  | 13700 BTU/hr
| 1065 BTU/lb |  | 1065 BTU/lb
| = 11.5 lb/hr |  | = 12.9 lb/hr | Moisture Removed
| 11.5 lb/hr |  | 12.9 lb/hr
| 8.3 lbs/gal |  | 8.3 lbs/gal
| = 1.4 gal/hr |  | = 1.6 gal/hr | Moisture Removed
| (SC x 1000/1.08) |  | (SC x 1000/1.08)
| CFM |  | CFM
| -(35.5 x 1000)/1.08 |  | -(21.4 x 1000)/1.08
| 1600 |  | 1600
| = -20.5 F |  | = -12.4 F | Sensible Cooling
Example 2:
| DR180 Normal Mode |  | DR180 Reheat Mode
| Conditions 95°F, 80/67°F |  | Conditions 95°F, 80/67°F
| CFM = 5600 |  | CFM = 5600
| TC = 176.6 KBTU |  | TC = 69.0 KBTU
| SC = 125.6 KBTU |  | SC = 13.0 KBTU
| Latent = 51.0 KBTU |  | Latent = 56.0 KBTU
| 51000 BTU/hr |  | 56000 BTU/hr
| 1065 BTU/lb |  | 1065 BTU/lb
| = 47.9 lb/hr |  | = 52.6 lb/hr | Moisture Removed
| 47.9 lb/hr |  | 52.6 lb/hr
| 8.3 lbs/gal |  | 8.3 lbs/gal
| = 5.8 gal/hr |  | = 6.3 gal/hr | Moisture Removed
| (SC x 1000/1.08) |  | (SC x 1000/1.08)
| CFM |  | CFM
| (125.6 x 1000/1.08) |  | (13 x 1000/1.08)
| 5600 |  | 5600
| = -20.8 F |  | = -2.1 F | Sensible Cooling

## Tool Example
MagnaDRY® Tool
Manufacturer: | York |  | Manufacturer: | York
Model: | DR036 |  | Model: | DR036
Unit Size (tons): | 3 |  | Unit Size (tons): | 3
Unit #1 | Normal Mode |  | Unit #2 | Reheat Mode
Entering dry bulb (DB) Temp | 80 | ºF | Entering dry bulb (DB) Temp | 80 | ºF
Entering wet bulb (WB) Temp | 67 | ºF | Entering wet bulb (WB) Temp | 67 | ºF
Ambient Temp | 97 | ºF | Ambient Temp | 97 | ºF
Airflow | 1200 | CFM | Airflow | 1200 | CFM
Total Capacity | 37.36 | KBTU | Total Capacity | 25.66 | KBTU
Sensible Capacity | 25.42 | KBTU | Sensible Capacity | 14.36 | KBTU
Latent | 11.94 | KBTU | Latent | 11.3 | KBTU
Moisture Removal | 11.3068 | lbs/hr | Moisture Removal | 10.7008 | lbs/hr
| 1.3623 | gal/hr |  | 1.2892 | gal/hr
Sensible Cooling of Conditioned Air °F | -19.5328 | °F | Sensible Cooling of Conditioned Air °F | -11.0343 | °F
Leaving dry bulb (DB) Temp | 60.4672 | ºF | Leaving dry bulb (DB) Temp | 68.9657 | ºF
Leaving wet bulb (WB) Temp | 57.1868 | ºF | Leaving wet bulb (WB) Temp | 60.4824 | ºF
Manufacturer: | Carrier |  | Manufacturer: | Carrier
Model: | 48HJ004 |  | Model: | 48HJ004
Unit Size (tons): | 3 |  | Unit Size (tons): | 3
Unit #1 | Normal Mode |  | Unit #2 | Reheat Mode
Entering DB Temp | 80 | ºF | Entering DB Temp | 80 | ºF
Entering WB Temp | 67 | ºF | Entering WB Temp | 67 | ºF
Ambient Temp | 97 | ºF | Ambient Temp | 97 | ºF
Airflow | 1200 | CFM | Airflow | 1200 | CFM
Total Capacity | 37.48 | KBTU | Total Capacity | 35.16 | KBTU
Sensible Capacity | 27.08 | KBTU | Sensible Capacity | 20.66 | KBTU
Latent | 10.4 | KBTU | Latent | 14.5 | KBTU
Moisture Removal | 9.8485 | lbs/hr | Moisture Removal | 13.7311 | lbs/hr
| 1.1866 | gal/hr |  | 1.6543 | gal/hr
Sensible Cooling of Conditioned Air °F | -20.8084 | °F | Sensible Cooling of Conditioned Air °F | -15.8752 | °F
Leaving DB Temp | 59.1916 | ºF | Leaving DB Temp | 64.1248 | ºF
Leaving WB Temp | 57.1204 | ºF | Leaving WB Temp | 57.819 | ºF
Assumptions:
Temp of R22 in a coil = 50°F @95°F Ambient, DB/WB 80/67°F
Latent Heat of water hfg = 1065 BTU/lb @ 50°F
Weight of water WtH20 = 8.3 lbs/gal
Enter model information in header boxes.
Enter unit performance data from the product technical guide.
Leaving air conditions will be displayed here.

## Tool
MagnaDRY® Tool
Manufacturer: |  |  | Manufacturer:
Model: |  |  | Model:
Unit Size (tons): |  |  | Unit Size (tons):
Unit #1 | Normal Mode |  | Unit #2 | Reheat Mode
Entering dry bulb (DB) Temp |  | ºF | Entering dry bulb (DB) Temp |  | ºF
Entering wet bulb (WB) Temp |  | ºF | Entering wet bulb (WB) Temp |  | ºF
Ambient Temp |  | ºF | Ambient Temp |  | ºF
Airflow |  | CFM | Airflow |  | CFM
Total Capacity |  | KBTU | Total Capacity |  | KBTU
Sensible Capacity |  | KBTU | Sensible Capacity |  | KBTU
Latent | 0 | KBTU | Latent | 0 | KBTU
Moisture Removal | 0 | lbs/hr | Moisture Removal | 0 | lbs/hr
| 0 | gal/hr |  | 0 | gal/hr
Sensible Cooling of Conditioned Air °F | #VALUE! | °F | Sensible Cooling of Conditioned Air °F | #VALUE! | °F
Leaving dry bulb (DB) Temp | #VALUE! | ºF | Leaving dry bulb (DB) Temp | #VALUE! | ºF
Leaving wet bulb (WB) Temp | 0 | ºF | Leaving wet bulb (WB) Temp | 0 | ºF
Manufacturer: |  |  | Manufacturer:
Model: |  |  | Model:
Unit Size (tons): |  |  | Unit Size (tons):
Unit #1 | Normal Mode |  | Unit #2 | Reheat Mode
Entering DB Temp |  | ºF | Entering DB Temp |  | ºF
Entering WB Temp |  | ºF | Entering WB Temp |  | ºF
Ambient Temp |  | ºF | Ambient Temp |  | ºF
Airflow |  | CFM | Airflow |  | CFM
Total Capacity |  | KBTU | Total Capacity |  | KBTU
Sensible Capacity |  | KBTU | Sensible Capacity |  | KBTU
Latent | 0 | KBTU | Latent | 0 | KBTU
Moisture Removal | 0 | lbs/hr | Moisture Removal | 0 | lbs/hr
| 0 | gal/hr |  | 0 | gal/hr
Sensible Cooling of Conditioned Air °F | #VALUE! | °F | Sensible Cooling of Conditioned Air °F | #VALUE! | °F
Leaving DB Temp | #VALUE! | ºF | Leaving DB Temp | #VALUE! | ºF
Leaving WB Temp | 0 | ºF | Leaving WB Temp | 0 | ºF
Assumptions:
Temp of R22 in a coil = 50°F @95°F Ambient, DB/WB 80/67°F
Latent Heat of water hfg = 1065 BTU/lb @ 50°F
Weight of water WtH20 = 8.3 lbs/gal